## Sample 1 (2)
Test | A25090E-Sample 1
Date | 2025-04-08
Manufacturer | Signify
Model | DR44328 XI020C070V054BSR5
Description | Load test, dimming test, start-up and flickering test. Signify - 20W Driver - 100 200 300 400 500 600 700mA - 10-54V with 5V step - 2 engineering samples
Current range | [100-700]mA
Voltage range | [10-54]V
Setpoints_programmed current | [100 200 300 400 500 600 700] mA
Setpoints_load voltage | [10 15 20 25 30 40 45 50 54] V
Requested by | Mohammad Abdul Wasay Ejaz
Tested by | Tamara Plohii , Mahya Naserzaeim
Test @120Vac | U in (V) | I in (A) | P in (W) | V out (V) | I out (A) | P out (W) | Efficiency(%) | THD(%) | Power Factor | Test @ 277 Vac | U in (V) | I in (A) | P in (W) | V out (V) | I out (A) | P out (W) | Efficiency(%) | THD(%) | Power Factor
Test @ 10V | 119.93 | 0.01836 | 1.733 | 10 | 0.098299 | 0.98238 | 56.6869 | 18.711 | 0.7871 | Test @ 10V | 277.12 | 0.019204 | 2.112 | 10.0001 | 0.098167 | 0.98177 | 46.4853 | 23.446 | 0.3968
| 119.94 | 0.030067 | 2.957 | 10 | 0.1981 | 1.9788 | 66.9176 | 12.698 | 0.82 |  | 277.2 | 0.022149 | 3.214 | 10 | 0.19775 | 1.9767 | 61.5013 | 19.672 | 0.5234
| 119.87 | 0.037306 | 4.06 | 10 | 0.29648 | 2.9642 | 73.0089 | 14.527 | 0.908 |  | 277.09 | 0.025009 | 4.333 | 10 | 0.29671 | 2.9681 | 68.4999 | 16.465 | 0.6252
| 119.89 | 0.04692 | 5.211 | 10 | 0.3969 | 3.9685 | 76.1554 | 12.889 | 0.9263 |  | 277.02 | 0.028115 | 5.472 | 10 | 0.39711 | 3.9706 | 72.562 | 14.169 | 0.7026
| 119.87 | 0.05577 | 6.368 | 10 | 0.49684 | 4.9659 | 77.9823 | 9.992 | 0.9526 |  | 276.93 | 0.03142 | 6.637 | 9.9999 | 0.49673 | 4.9669 | 74.8372 | 12.291 | 0.7628
| 119.88 | 0.06536 | 7.544 | 9.9999 | 0.5966 | 5.9675 | 79.1021 | 9.216 | 0.9628 |  | 276.88 | 0.03473 | 7.814 | 10 | 0.59692 | 5.9684 | 76.381 | 11.731 | 0.8126
| 119.86 | 0.07546 | 8.738 | 9.9999 | 0.69626 | 6.9625 | 79.6805 | 10.406 | 0.966 |  | 276.88 | 0.03838 | 9.016 | 10 | 0.69662 | 6.9637 | 77.2376 | 10.482 | 0.8486
Test @ 15V | 119.88 | 0.035922 | 3.907 | 15.0006 | 0.19755 | 2.963 | 75.8376 | 14.765 | 0.9074 | Test @ 15V | 277.09 | 0.020568 | 2.619 | 15.0006 | 0.098031 | 1.4712 | 56.1734 | 21.635 | 0.4596
| 119.88 | 0.035922 | 3.907 | 15.0006 | 0.19755 | 2.963 | 75.8376 | 14.765 | 0.9074 |  | 277.08 | 0.0246 | 4.188 | 15.0007 | 0.19733 | 2.9603 | 70.6852 | 16.733 | 0.6144
| 119.86 | 0.050166 | 5.635 | 15.0006 | 0.2963 | 4.4428 | 78.8422 | 11.948 | 0.937 |  | 277.08 | 0.0246 | 4.188 | 15.0007 | 0.19733 | 2.9603 | 70.6852 | 16.733 | 0.6144
| 119.88 | 0.0633 | 7.3 | 15.0006 | 0.39645 | 5.9498 | 81.5039 | 9.114 | 0.962 |  | 276.89 | 0.033947 | 7.56 | 15.0006 | 0.39666 | 5.9475 | 78.6702 | 11.794 | 0.8043
| 119.87 | 0.07771 | 8.988 | 15.0006 | 0.49646 | 7.4489 | 82.8765 | 10.337 | 0.9649 |  | 276.89 | 0.03908 | 9.262 | 15.0006 | 0.4967 | 7.4494 | 80.4295 | 10.832 | 0.8561
| 119.86 | 0.09192 | 10.69 | 15.0007 | 0.59657 | 8.9482 | 83.7064 | 12.31 | 0.9704 |  | 276.87 | 0.04478 | 10.969 | 15.0007 | 0.59673 | 8.9513 | 81.6057 | 8.576 | 0.8847
| 119.84 | 0.10601 | 12.427 | 15.0006 | 0.69604 | 10.4428 | 84.0333 | 10.798 | 0.9782 |  | 276.89 | 0.05053 | 12.693 | 15.0006 | 0.69618 | 10.4453 | 82.2915 | 7.367 | 0.9072
Test @ 20V | 119.94 | 0.029108 | 2.855 | 19.9999 | 0.098068 | 1.9578 | 68.5758 | 14.541 | 0.8177 | Test @ 20V | 277.04 | 0.0219 | 3.119 | 19.9999 | 0.097791 | 1.9568 | 62.7382 | 19.941 | 0.5141
| 119.88 | 0.045378 | 5.004 | 19.9999 | 0.19721 | 3.9445 | 78.8273 | 13.436 | 0.9199 |  | 277.05 | 0.02764 | 5.263 | 19.9999 | 0.19733 | 3.9422 | 74.9038 | 14.566 | 0.6872
| 119.89 | 0.0626 | 7.204 | 20 | 0.29642 | 5.928 | 82.2874 | 9.528 | 0.9599 |  | 276.88 | 0.033632 | 7.458 | 20 | 0.29668 | 5.9315 | 79.5322 | 11.933 | 0.8009
| 119.85 | 0.08165 | 9.405 | 19.9999 | 0.39625 | 7.9244 | 84.257 | 12.234 | 0.9612 |  | 276.86 | 0.040383 | 9.664 | 19.9998 | 0.3966 | 7.9313 | 82.0701 | 10.074 | 0.8644
| 119.85 | 0.0994 | 11.621 | 20 | 0.49668 | 9.9271 | 85.4235 | 11.254 | 0.9755 |  | 276.77 | 0.04792 | 11.89 | 19.9999 | 0.49637 | 9.9283 | 83.5013 | 7.944 | 0.8964
| 119.83 | 0.11817 | 13.872 | 19.9999 | 0.59639 | 11.9282 | 85.9877 | 11.296 | 0.9796 |  | 276.86 | 0.05519 | 14.134 | 19.9998 | 0.59655 | 11.9312 | 84.4145 | 6.872 | 0.925
| 119.82 | 0.13722 | 16.144 | 19.9999 | 0.69597 | 13.92 | 86.2238 | 11.574 | 0.9819 |  | 276.91 | 0.06296 | 16.378 | 19.9998 | 0.69602 | 13.9198 | 84.991 | 6.534 | 0.9394
Test @ 25V | 119.93 | 0.033081 | 3.321 | 25.0006 | 0.097911 | 2.4432 | 73.5669 | 12.054 | 0.837 | Test @ 25V | 277.01 | 0.023061 | 3.594 | 25.0005 | 0.097825 | 2.4486 | 68.1304 | 18.408 | 0.5626
| 119.87 | 0.053257 | 6.047 | 25.0006 | 0.19742 | 4.9361 | 81.6288 | 10.697 | 0.9472 |  | 276.99 | 0.030644 | 6.308 | 25.0006 | 0.19717 | 4.9324 | 78.1935 | 12.689 | 0.7431
| 119.86 | 0.076 | 8.77 | 25.0006 | 0.29636 | 7.4111 | 84.5051 | 10.834 | 0.9627 |  | 276.86 | 0.038421 | 9.039 | 25.0006 | 0.29655 | 7.4119 | 81.9989 | 10.129 | 0.8497
| 119.84 | 0.09852 | 11.505 | 25.0006 | 0.39656 | 9.9148 | 86.1778 | 11.509 | 0.9744 |  | 276.87 | 0.047547 | 11.767 | 25.0005 | 0.39675 | 9.9186 | 84.292 | 7.675 | 0.8938
| 119.83 | 0.12178 | 14.279 | 25.0007 | 0.49645 | 12.4107 | 86.916 | 12.214 | 0.9786 |  | 276.84 | 0.05668 | 14.538 | 25.0006 | 0.49664 | 12.4107 | 85.3675 | 6.764 | 0.9265
| 119.79 | 0.14478 | 17.065 | 25.0006 | 0.59658 | 14.9131 | 87.3899 | 10.893 | 0.984 |  | 276.9 | 0.06639 | 17.284 | 25.0006 | 0.59656 | 14.9141 | 86.2885 | 7.551 | 0.9402
| 119.78 | 0.16803 | 19.89 | 25.0006 | 0.69605 | 17.406 | 87.5115 | 9.129 | 0.9882 |  | 276.89 | 0.07611 | 20.058 | 25.0006 | 0.69605 | 17.401 | 86.7536 | 7.746 | 0.9518
Test @ 30V | 119.88 | 0.034957 | 3.813 | 29.9999 | 0.097813 | 2.939 | 77.0783 | 14.801 | 0.9098 | Test @ 30V | 277.04 | 0.024332 | 4.097 | 29.9999 | 0.09797 | 2.9372 | 71.6926 | 16.927 | 0.6078
| 119.87 | 0.06148 | 7.079 | 30 | 0.19743 | 5.9268 | 83.7234 | 9.183 | 0.9606 |  | 276.91 | 0.033319 | 7.345 | 29.9998 | 0.19714 | 5.913 | 80.5041 | 12.029 | 0.7961
| 119.86 | 0.08924 | 10.333 | 29.9999 | 0.29663 | 8.8946 | 86.0796 | 13.176 | 0.9661 |  | 276.87 | 0.043691 | 10.609 | 29.9999 | 0.29688 | 8.907 | 83.9568 | 8.47 | 0.877
| 119.83 | 0.11617 | 13.636 | 29.9999 | 0.39649 | 11.8953 | 87.2343 | 10.82 | 0.9798 |  | 276.89 | 0.054476 | 13.885 | 29.9998 | 0.39686 | 11.9088 | 85.7674 | 7.415 | 0.9205
| 119.79 | 0.14379 | 16.943 | 29.9999 | 0.49678 | 14.9035 | 87.9627 | 10.992 | 0.9836 |  | 276.81 | 0.06598 | 17.161 | 29.9998 | 0.49652 | 14.8948 | 86.7942 | 7.392 | 0.9396
| 119.78 | 0.17137 | 20.286 | 29.9998 | 0.59667 | 17.8959 | 88.2182 | 9.115 | 0.9883 |  | 276.89 | 0.07753 | 20.445 | 29.9999 | 0.59657 | 17.9033 | 87.568 | 7.992 | 0.9524
| 119.74 | 0.19952 | 23.686 | 29.9999 | 0.69637 | 20.895 | 88.2168 | 8.424 | 0.9914 |  | 276.88 | 0.08926 | 23.73 | 29.9998 | 0.69633 | 20.896 | 88.0572 | 6.295 | 0.9601
Test @ 35V | 119.86 | 0.039741 | 4.336 | 35.0005 | 0.097903 | 3.4258 | 79.0091 | 13.287 | 0.9104 | Test @ 35V | 276.98 | 0.025862 | 4.619 | 35.0006 | 0.09783 | 3.4215 | 74.0746 | 15.863 | 0.6448
| 119.87 | 0.07049 | 8.125 | 35.0006 | 0.19731 | 6.91 | 85.0457 | 11.273 | 0.9616 |  | 276.89 | 0.036326 | 8.396 | 35.0006 | 0.19726 | 6.9021 | 82.2071 | 11.652 | 0.8347
| 119.84 | 0.10203 | 11.925 | 35.0006 | 0.29664 | 10.3857 | 87.092 | 11.171 | 0.9752 |  | 276.86 | 0.048887 | 12.191 | 35.0005 | 0.29675 | 10.3955 | 85.2718 | 7.935 | 0.9007
| 119.81 | 0.13421 | 15.759 | 35.0006 | 0.39683 | 13.8936 | 88.163 | 12.071 | 0.9801 |  | 276.88 | 0.06163 | 15.979 | 35.0005 | 0.39713 | 13.9019 | 87.0011 | 6.495 | 0.9365
| 119.77 | 0.16593 | 19.628 | 35.0007 | 0.497 | 17.3929 | 88.6129 | 9.291 | 0.9877 |  | 276.79 | 0.07512 | 19.798 | 35.0006 | 0.497 | 17.3984 | 87.8794 | 6.388 | 0.9517
| 119.76 | 0.19831 | 23.54 | 35.0006 | 0.5969 | 20.9027 | 88.7964 | 8.393 | 0.9912 |  | 276.87 | 0.08876 | 23.595 | 35.0006 | 0.59698 | 20.8963 | 88.5625 | 6.284 | 0.9601
| 119.75 | 0.1986 | 23.577 | 35.0005 | 0.59798 | 20.9317 | 88.7803 | 8.383 | 0.9913 |  | 276.88 | 0.08888 | 23.632 | 35.0006 | 0.59846 | 20.9448 | 88.6291 | 6.299 | 0.9603
Test @ 40V | 119.9 | 0.044262 | 4.876 | 39.9998 | 0.097875 | 3.9169 | 80.3302 | 13.349 | 0.9188 | Test @ 40V | 276.85 | 0.027373 | 5.158 | 39.9999 | 0.097855 | 3.9144 | 75.8895 | 14.743 | 0.6806
| 119.87 | 0.07941 | 9.156 | 39.9998 | 0.19739 | 7.8973 | 86.2528 | 11.265 | 0.962 |  | 276.86 | 0.039562 | 9.421 | 39.9998 | 0.19729 | 7.8886 | 83.7341 | 10.572 | 0.8602
| 119.83 | 0.11536 | 13.54 | 39.9999 | 0.29711 | 11.8796 | 87.7372 | 10.728 | 0.9795 |  | 276.88 | 0.054215 | 13.79 | 39.9999 | 0.29698 | 11.8818 | 86.1624 | 7.542 | 0.9187
| 119.81 | 0.15164 | 17.893 | 39.9998 | 0.39709 | 15.8839 | 88.7714 | 10.451 | 0.9849 |  | 276.91 | 0.06907 | 18.089 | 39.9999 | 0.39734 | 15.8928 | 87.8591 | 7.51 | 0.9458
| 119.76 | 0.18828 | 22.326 | 39.9998 | 0.4973 | 19.8945 | 89.109 | 8.522 | 0.9902 |  | 276.77 | 0.08436 | 22.411 | 39.9998 | 0.49736 | 19.8938 | 88.7681 | 6.414 | 0.9598
| 119.75 | 0.19739 | 23.428 | 39.9999 | 0.52204 | 20.888 | 89.1582 | 8.355 | 0.9912 |  | 276.87 | 0.08835 | 23.487 | 39.9999 | 0.52198 | 20.8801 | 88.9005 | 6.297 | 0.9601
| 119.74 | 0.19792 | 23.493 | 39.9999 | 0.52372 | 20.949 | 89.1711 | 8.33 | 0.9914 |  | 276.88 | 0.08832 | 23.483 | 39.9998 | 0.52237 | 20.8871 | 88.9458 | 6.319 | 0.9603
Test @ 45V | 119.89 | 0.048413 | 5.406 | 45.0006 | 0.098072 | 4.413 | 81.6321 | 12.411 | 0.9313 | Test @ 45V | 276.89 | 0.028612 | 5.664 | 45.0006 | 0.097896 | 4.4033 | 77.7412 | 13.702 | 0.715
| 119.86 | 0.0878 | 10.163 | 45.0005 | 0.19738 | 8.8882 | 87.4568 | 13.284 | 0.9656 |  | 276.92 | 0.043142 | 10.439 | 45.0005 | 0.19765 | 8.8869 | 85.1321 | 8.459 | 0.8738
| 119.83 | 0.12908 | 15.135 | 45.0006 | 0.29733 | 13.3737 | 88.3628 | 12.421 | 0.9785 |  | 276.9 | 0.05965 | 15.368 | 45.0006 | 0.29745 | 13.3887 | 87.1209 | 7.671 | 0.9305
| 119.78 | 0.16936 | 20.038 | 45.0005 | 0.39748 | 17.8868 | 89.2646 | 9.256 | 0.9878 |  | 276.9 | 0.07663 | 20.198 | 45.0005 | 0.39777 | 17.904 | 88.6425 | 7.675 | 0.9519
| 119.76 | 0.19716 | 23.401 | 45.0005 | 0.46539 | 20.9375 | 89.4726 | 8.461 | 0.9911 |  | 276.8 | 0.08827 | 23.46 | 45.0005 | 0.46542 | 20.9465 | 89.2862 | 6.272 | 0.9601
| 119.74 | 0.19708 | 23.39 | 45.0006 | 0.46536 | 20.9435 | 89.5406 | 8.34 | 0.9912 |  | 276.87 | 0.08802 | 23.399 | 45.0006 | 0.46411 | 20.8901 | 89.2777 | 6.304 | 0.9602
| 119.75 | 0.19658 | 23.334 | 45.0006 | 0.46421 | 20.8877 | 89.5163 | 8.385 | 0.9911 |  | 276.87 | 0.08779 | 23.341 | 45.0005 | 0.46328 | 20.8409 | 89.2886 | 6.315 | 0.9603
Test @ 50V | 119.88 | 0.051929 | 5.892 | 49.9999 | 0.098005 | 4.8943 | 83.0666 | 10.537 | 0.9462 | Test @ 50V | 276.91 | 0.030104 | 6.156 | 49.9999 | 0.097897 | 4.8983 | 79.5691 | 12.765 | 0.7385
| 119.85 | 0.09695 | 11.308 | 49.9999 | 0.19878 | 9.9467 | 87.962 | 11.765 | 0.9732 |  | 276.86 | 0.04694 | 11.587 | 49.9998 | 0.19899 | 9.9477 | 85.8519 | 7.681 | 0.8916
| 119.81 | 0.14217 | 16.734 | 49.9998 | 0.29752 | 14.8739 | 88.8841 | 11.328 | 0.9825 |  | 276.89 | 0.06516 | 16.942 | 49.9999 | 0.29762 | 14.8903 | 87.8899 | 7.021 | 0.9389
| 119.77 | 0.18718 | 22.195 | 49.9998 | 0.39768 | 19.8939 | 89.6322 | 8.565 | 0.99 |  | 276.92 | 0.08396 | 22.29 | 49.9998 | 0.3978 | 19.8882 | 89.2246 | 6.491 | 0.9587
| 119.76 | 0.19597 | 23.257 | 49.9998 | 0.41729 | 20.8664 | 89.7209 | 8.476 | 0.9909 |  | 276.78 | 0.08773 | 23.318 | 49.9998 | 0.41748 | 20.8733 | 89.5158 | 6.283 | 0.9603
| 119.76 | 0.1959 | 23.25 | 49.9998 | 0.41746 | 20.8609 | 89.7243 | 8.433 | 0.991 |  | 276.87 | 0.08739 | 23.235 | 49.9999 | 0.41619 | 20.8011 | 89.5247 | 6.272 | 0.9603
| 119.76 | 0.19516 | 23.162 | 49.9998 | 0.41595 | 20.8033 | 89.8167 | 8.438 | 0.991 |  | 276.87 | 0.08754 | 23.275 | 49.9998 | 0.41675 | 20.8452 | 89.5603 | 6.285 | 0.9603
Test @ 54V | 119.89 | 0.05541 | 6.321 | 53.9995 | 0.098074 | 5.2989 | 83.8296 | 10.082 | 0.9516 | Test @ 54V | 276.84 | 0.031201 | 6.574 | 53.9995 | 0.098181 | 5.2911 | 80.485 | 12.305 | 0.7611
| 119.84 | 0.10411 | 12.179 | 53.9995 | 0.19892 | 10.7463 | 88.2366 | 11.257 | 0.9761 |  | 276.86 | 0.04977 | 12.436 | 53.9995 | 0.19901 | 10.738 | 86.3459 | 7.704 | 0.9025
| 119.8 | 0.15264 | 18.01 | 53.9995 | 0.2976 | 16.0695 | 89.2256 | 10.443 | 0.9849 |  | 276.91 | 0.06944 | 18.207 | 53.9995 | 0.29782 | 16.0794 | 88.3146 | 7.24 | 0.9468
| 119.75 | 0.19526 | 23.166 | 53.9995 | 0.38519 | 20.799 | 89.7825 | 8.474 | 0.9908 |  | 276.87 | 0.08737 | 23.231 | 53.9995 | 0.38551 | 20.8104 | 89.5804 | 6.264 | 0.9603
| 119.75 | 0.1948 | 23.115 | 53.9995 | 0.38475 | 20.7761 | 89.8812 | 8.463 | 0.9909 |  | 276.79 | 0.08705 | 23.141 | 53.9995 | 0.384 | 20.7396 | 89.6226 | 6.246 | 0.9604
| 119.76 | 0.19439 | 23.067 | 53.9996 | 0.38424 | 20.7475 | 89.9444 | 8.448 | 0.9908 |  | 276.86 | 0.08721 | 23.187 | 53.9995 | 0.38492 | 20.787 | 89.6492 | 6.287 | 0.9604
| 119.76 | 0.19439 | 23.069 | 53.9995 | 0.38391 | 20.737 | 89.8912 | 8.446 | 0.9909 |  | 276.89 | 0.08737 | 23.234 | 53.9996 | 0.38573 | 20.8235 | 89.6252 | 6.306 | 0.9603